PowerIT Vacuum Cast Coil Dry Type 
Distribution Transformers

Ventilation of transformer room

When the transformer is mounted inside a room, the ventilation of the room must be properly ensured in order to evacuate the heat released by the transformer.

The following points should be taken into consideration:

1) Clearances from the transformer to the walls and cell of the room:

( Transformer without enclosure:

The minimum clearances from the HV phases (resin isolated parts) to the walls will be according to the highest voltage of the equipment:

| Highest voltage, serie (kV) | mm |
| --- | --- |
| 12 | 50 |
| 24 | 120 |
| 36 | 200 |

The minimum clearances from the live parts (HV&LV connections or terminals) to the walls and cell of the room will be according to the local installation regulations. Nevertheless we recommend the following:

| Highest voltage, serial (kV) | mm |
| --- | --- |
| 12 | 110 |
| 24 | 210 |
| 36 | 280 |

( Transformer with enclosure:

The minimum clearances from any part of the enclosure to the walls or cell of the room will be 350 mm.

2) NATURAL VENTILATION: Input E and output S ventilation surfaces in the room:

The minimum input E and output S ventilation surfaces will be according to the following formulas expressed in m2.

where:

Total losses in kW (no load losses + load losses)

Vertical distance between the centers of the openings, expressed in meters.

The following should be avoided:

- The transformer should not be installed in small rooms with blinds or metallic walls exposed to direct sunlight.

- The air for cooling the transformer should not be aspired or expelled in the same room in which it is installed.

- The transformer should not be installed in premises that are destined for other uses; in particular in those in which there are machines that work at high temperatures: boilers, steam generators, …

If the transformer cannot be installed in premises with sufficient natural ventilation, forced ventilation should be used.

3) FORCED VENTILATION IN THE ROOM:

If the natural ventilation in the room is not enough, air extractors will be installed ensuring in general the following flow:

3,5 m3/minute each kW of total losses.

Example:

Total losses (no load + load losses) = 12 kW => Flow required in the extractors 42 m3/minute = 2520 m3/hour

# Text boxes



Industrial IT Enabled products from ABB are the building blocks for greater productivity, featuring all the tools necessary for lifecycle product support in consistent electronic form.